WATER SYSTEM INSPECTION REPORT

STATE ID# 1790

WA0000287

DATE: May 11, 2021

NAME: Weber Valley Heights Association

LOCATION: 44135 Perryman Lane Hemet, CA 94544 (APN 571-040-004)

MAILING ADDRESS: 	Jeff Hall 44350 E. Benton Road, Hemet, CA 92543

Robert Franko & Debbie St. Pierre 44135 Perryman Lane Hemet, CA 92544

OWNER\OPERATOR:  	President Jeff Hall 951-767-7072 home, 951-313-2249 cell

Robert Franko, Vice President 951-764-5081

Secretary / Treasurer Deborah St. Pierre 951-764-5059

Dan Spears, Maintenance 909-770-0852

TYPE OF SYSTEM

This is a State Small water system with two wells and 2 pressure zones.  There are 6 connections on each well.  There is approximately 15 permantent residents.  No future dedevelopment is planned at the community.

This is a routine inspection conducted  by Daisy Ciudad Real  with the assistance of  Deborah St. Pierre, Robert Franko.

SOURCES OF WATER AND STORAGE FACILITIES

Well No. 1

- This Department does not have construction records.

- Well production is unknown

- Based on information provided by owner this well is 352 feet deep.  Riverside County well permit #29372 was assigned for inventory purposes only.

- Records show this well has nitrate levels that are 50% the MCL and must be sampled yearly.

Well No. 2

- This Well was constructed in December 1990, under Riverside County well permit #29371.  The well is 600 feet deep with a 50ft sanitary seal.

- The well produces approximately 9 GPM

Storage:

- This system has 3 different storage tanks.

Distribution: The distribution for this system is composed of a 2” pipe that runs from well #1 through Ginger circle to Wrench Road to the two tanks at Happy Hills lane.  Same size pipe runs from well 2 to the metal tank half way up the road.

TDS was measured at 250 mg/L by conductivity at hose bib by metal tank.

CHEMICAL QUALITY

| Location | Nitrate as N (µg/L) Due every year | Inorganic chemical Due every 9 years |
| --- | --- | --- |
| Well 1 | 2017 | 2013 |
| Well 2 | 2017 | 2013 |

BACTERIOLOGICAL QUALITY

Bacteriological sampling has not been satisfactory for the past year. Next samples are due in the 2nd quarter of 2021.

CORRECTIONS & RECOMMENDATIONS:

Submit documents and pictures to show correction for the following by 7/30/2021

- Install back flow prevention devices at hose bibs at wells and remove threads at sampling bibs.

- Seal pass through holes on electrical boxes at both wells. (repeat violations)

Submit by 12/2021

- Submit the yearly notification and proof of delivery by 12/2021

- Sample well #1 and #2 for inorganic chemicals sampling was last conducted in 2013.  This sampling is due every 9 years.

Please contact this Department with additional questions at 951-955-8980

REPORT PREPARED BY:

Daisy Ciudad Real, R.E.H.S., M.P.H.

DATE: 5/12/2021